## 2020 Second Half
Michigan Public Service Commission
2020 Second Half Inspection
Question ID | Question Text | Compliance | Sort Order
192.16(b)(1)_P | Where an operator does not maintain the customer's buried piping up to the entry of the first building, equipment or fence, do procedures require each customer be notified once in writing that the operator does not maintain the customer's buried piping? |  | 01860
192.16(b)(2)_P | Where an operator does not maintain the customer's buried piping up to the entry of the first building, equipment or fence, do procedures require each customer be notified once in writing that if the customer's buried piping is not maintained, it may be subject to the potential hazards of corrosion and leakage? |  | 01890
192.16(b)(3)(i)_P | Where an operator does not maintain the customer's buried piping up to the entry of the first building, equipment or fence, do procedures require each customer be notified once in writing that buried gas piping should be periodically inspected for leaks? |  | 01920
192.16(b)(3)(ii)_P | Where an operator does not maintain the customer's buried piping up to the entry of the first building, equipment or fence, do procedures require each customer be notified once in writing that buried gas piping should be periodically inspected for corrosion if the piping is metallic? |  | 01950
192.16(b)(3)(iii)_P | Where an operator does not maintain the customer's buried piping up to the entry of the first building, equipment or fence, do procedures require each customer be notified once in writing that buried gas piping should be repaired if any unsafe condition is discovered? |  | 01970
192.16(b)(4)_P | Where an operator does not maintain the customer's buried piping up to the entry of the first building, equipment or fence, do procedures require each customer be notified once in writing that when excavating near buried gas piping, the piping should be located in advance and the excavation done by hand? |  | 02010
192.16(b)(5)_P | Where an operator does not maintain the customer's buried piping up to the entry of the first building, equipment or fence, do procedures require each customer be notified once in writing that the operator (if applicable), plumbing contractors, and heating contractors can assist in locating, inspecting, and repairing the customer?s buried piping? |  | 02040
192.16(c)_P | Where an operator does not maintain the customer's buried piping up to the entry of the first building, equipment or fence, do procedures require each customer be notified 90 days after they first receive gas at a particular location of the messages in 192.16? Do procedures allow operators of master meter systems to continuously post a general notice in a prominent location frequented by customers? |  | 02070
192.16(d)(1)_R | Where an operator does not maintain the customer's buried piping up to the entry of the first building, equipment or fence, is the current copy of the notice used to comply with 192.16 available for inspection? |  | 02110
192.16(d)(2)_R | Where an operator does not maintain the customer's buried piping up to the entry of the first building, equipment or fence, do records document that notices have been sent to customers within the previous 3 years? |  | 02140
192.381(a)(1)_P | Do procedures require that specifications ensure the EFV will function properly up to the maximum operating pressure at which the valve is rated? |  | 21720
192.381(a)(2)_P | Do procedures require that specifications ensure that the EFV will function properly at all temperatures reasonably expected in the operating environment of the service line? |  | 21750
192.381(a)(3)(i)_P | Do procedures require that specifications ensure that the EFV will, at 10 psig, close at or not more than 50% above, the rated closure flow rate specified by the manufacturer? |  | 21780
192.381(a)(3)(ii)_P | Do procedures require that specifications ensure that the EFV designed to allow pressure to equalize across the valve will, upon closure, reduce gas flow to no more than 5% of the manufacturer's specified closure flow rate, up to a maximum of 20 cubic feet per hour? Do procedures require that specifications ensure that the EFV not designed to allow pressure to equalize across the valve will, upon closure, reduce gas flow to no more than 0.4 cubic feet per hour? |  | 21810
192.381(a)(4)_P | Do procedures require the manufacturer specifications or tests ensure that the EFV will not close when the pressure is less than the manufacturer's minimum specified operating pressure, and the flow rate is below the manufacturer's minimum specified closure flow rate for EFVs used on single residence service lines that operate continuously throughout the year at a pressure not less than 10 psig? |  | 21840
192.381(b)_P | Do procedures require EFVs meet the applicable requirements of 49 CFR 192 Subpart B and D? |  | 21870
192.381(c)_P | Do procedures require the EFVs on services line be marked or otherwise identified? |  | 21900
192.381(c)_O | Are EFVs on the service line marked or otherwise identified? |  | 21940
192.381(d)_P | Do procedures require that EFVs be located as near as practical to the fitting connecting the service line to its source of gas supply? |  | 21960
192.381(d)_O | Are EFVs located as near as practical to the fitting connecting the service line to its source of gas supply? |  | 22000
192.381(e)_P | Do procedures discourage installing an EFV on a service line where the operator has prior experience with contaminants in the gas stream, where these contaminants could be expected to cause the EFV to malfunction, or where the EFV would interfere with necessary operation and maintenance activities on the service, such as blowing liquids from the line? |  | 22020
192.383(b)_P | Do procedures require an EFV be installed on any new or replaced service line serving a single-family residence (a single EFV may be installed to protect both service lines on a branch service), a multifamily residence, or small commercial customers with loads not exceeding 1,000 SCFH at time of installation? Exceptions: the service line does not operate at a pressure of 10 psig or greater; there is prior experience with gas contaminants that could interfere with the EFV; an EFV could interfere with necessary O&M activities; an EFV meeting 192.381 is not commercially available. |  | 22050
192.383(b)_O | Are EFVs installed on any new or replaced service line serving a single-family residence(a single EFV may be installed to protect both service lines on a branch service), a multifamily residence, or small commercial customers with loads not exceeding 1,000 SCFH at time of installation? Exceptions: the service line does not operate at a pressure of 10 psig or greater; there is prior experience with gas contaminants that could interfere with the EFV; an EFV could interfere with necessary O&M activities; an EFV meeting 192.381 is not commercially available. |  | 22090
192.383(d)_P | Do procedures require that EFVs be installed where the customer has requested? Exceptions: the service line does not operate at a pressure of 10 psig or greater; there is prior experience with gas contaminants that could interfere with the EFV; an EFV could interfere with necessary O&M activities; an EFV meeting 192.381 is not commercially available. |  | 22125
192.383(d)_R | Do records document that EFVs were installed where the customer has requested? Exceptions: the service line does not operate at a pressure of 10 psig or greater; there is prior experience with gas contaminants that could interfere with the EFV; an EFV could interfere with necessary O&M activities; an EFV meeting 192.381 is not commercially available. |  | 22127
192.383(e)(1)_P | Do procedures require that operator notify customers of their right to request an EFV via written or electronic notification? Master-meter systems and liquefied petroleum gas (LPG) operators with fewer than 100 customers may continuously post a general notification in a prominent location frequented by customers. Notification is not required where the service line does not operate at a pressure of 10 psig or greater; there is prior experience with gas contaminants that could interfere with the EFV; an EFV could interfere with necessary O&M activities; an EFV meeting 192.381 is not commercially available. |  | 22130
192.383(e)(1)_R | Do records document that operator has notified customers of their right to request an EFV via written or electronic notification, which may include emails, Web site postings, and e- billing notices? Master-meter systems and liquefied petroleum gas (LPG) operators with fewer than 100 customers may continuously post a general notification in a prominent location frequented by customers. Notification is not required where the service line does not operate at a pressure of 10 psig or greater; there is prior experience with gas contaminants that could interfere with the EFV; an EFV could interfere with necessary O&M activities; an EFV meeting 192.381 is not commercially available. |  | 22133
192.383(e)(2)_R | Does the notification required in 192.383 (e) (1) include an explanation of the potential safety benefits that may be derived from installing an EFV, including information that an EFV is designed to shut off the flow of natural gas automatically if the service line breaks? |  | 22136
192.383(e)(3)_R | Does the notification required in 192.383 (e) (1) include a description of EFV installation and replacement costs, including costs for maintaining and replacing an EFV that may later be incurred, and to the extent known, what those costs will be? |  | 22139
192.383(e)(4)_R | Does the notification required in 192.383 (e) (1) indicate that if a customer requests installation of an EFV, and the load does not exceed 1,000 SCFH and no exceptions are present, the operator must install an EFV at a mutually agreeable date? Exceptions: the service line does not operate at a pressure of 10 psig or greater; there is prior experience with gas contaminants that could interfere with the EFV; an EFV could interfere with necessary O&M activities; an EFV meeting 192.381 is not commercially available. |  | 22142
192.383(f)_R | Is the current notice or notices available during pipeline safety inspections? |  | 22145
192.383(g)_R | Does the annual report document the detailed EFV measures? |  | 22148
192.385(b)_P | Do procedures require installation of either a manual service line shut-off valve, or an EFV, if available, on any new or replaced service line with a meter capacity exceeding 1,000 SCFH? |  | 22190
192.385(c)_P | Do procedures require manual service line shut-off valves be installed in such a way as to allow accessibility during emergencies? Do procedures require manual service line shut-off valves to be subjected to regular scheduled maintenance that is consistent with the valve manufacturer's specifications? |  | 22203
192.385(c)_R | Do records document maintenance of manual service line shut-off valves? |  | 22206
192.385(c)_O | Are manual service line shut-off valves installed so as to be accessible during emergencies? Is maintenance performed on manual service line shut-off valves? |  | 22208
192.605(b)(11)_P | Do procedures require the operator to promptly respond to a report of gas odor inside or near a building? |  | 31480
192.605(b)(11)_R | Do records document the operator has promptly responded to a report of gas odor inside or near a building? |  | 31490
192.605(b)(11)_O | Does the operator promptly respond to a report of gas odor inside or near a building? |  | 31500
192.614(a)_P | Is there a written damage prevention program? (see exceptions) |  | 33130
192.614(b)_P | Does the operator participate in a one-call system (MISS DIG 811 or equivalent)? |  | 33160
192.614(c)(1)_R | Do records document the damage prevention program include the identity, on a current basis, of persons who normally engage in excavation activities in the area in which pipeline is located? |  | 33220
192.614(c)(2)(i)_P | Do procedures require that the damage prevention program notify the public, and persons who normally engage in excavation activities in the area in which the pipeline is located, of the program's existence and purpose? |  | 33250
192.614(c)(2)(i)_R | Do records document that the damage prevention program notified the public, and persons who normally engage in excavation activities in the area in which the pipeline is located, of the program's existence and purpose? |  | 33280
192.614(c)(2)(ii)_P | Do procedures require that the damage prevention program notify the public, and persons who normally engage in excavation activities in the area in which the pipeline is located, how to learn the location of underground pipelines before excavation activities? |  | 33310
192.614(c)(2)(ii)_R | Do records document that the damage prevention program notified the public, and persons who normally engage in excavation activities in the area in which the pipeline is located, how to learn the location of underground pipelines before excavation activities? |  | 33340
192.614(c)(3)_P | Do procedures require the damage prevention program provide a means of receiving and recording notification of planned excavation activities? |  | 33370
192.614(c)(3)_R | Do records document notification was received of planned excavation activities? |  | 33400
192.614(c)(3)_R | Do records document notification was received of planned excavation activities? |  | 33400
192.614(c)(4)_P | Do procedures require the damage prevention program provide actual notification of the type of markings and how to identify the markings where an operator has a buried pipeline? |  | 33430
192.614(c)(4)_P | Do procedures require the damage prevention program provide actual notification of the type of markings and how to identify the markings where an operator has a buried pipeline? |  | 33430
192.614(c)(4)_R | Do records document the damage prevention program provides actual notification of the type of markings and how to identify the markings where an operator has a buried pipeline? |  | 33460
192.614(c)(4)_R | Do records document the damage prevention program provides actual notification of the type of markings and how to identify the markings where an operator has a buried pipeline? |  | 33460
192.614(c)(5)_P | Do procedures require the damage prevention program to provide temporary marking of buried pipelines in the area of excavation before activities begin? |  | 33490
192.614(c)(5)_R | Do records document that areas of excavation were marked prior to beginning of activities? |  | 33520
192.614(c)(5)_O | Does the operator mark areas of excavation prior to beginning of activities? |  | 33524
192.614(c)(6)_P | When an operator has reason to believe excavation activities could damage pipelines, do procedures require inspections be done as frequently as necessary during and after activities to verify the integrity of the pipeline? Where the excavation activities include blasting, do procedures require the inspections include leak survey? |  | 33530
192.614(c)(6)_R | Do records document that additional inspections were done as necessary during excavation activities the operator believes could damage pipeline? Where the excavation activities include blasting, do records document the inspections include leak survey? |  | 33535
R 460.20421(a)_P | SOUR GAS: Do procedures require an operator to monitor excavation activity using on-site personnel when excavation activities are taking place within a sour gas pipeline right-of-way? |  | 33670
R 460.20421(a)_R | SOUR GAS: Do records document that on-site operator personnel monitored excavation activity occurring within a sour gas pipeline right-of-way? |  | 33700
R 460.20421(b)_P | SOUR GAS: Do procedures require the operator to notify the excavator of the inherent hazards in the release of sour gas when responding to requests to mark pipeline location? |  | 33730
R 460.20421(b)_R | SOUR GAS: Do records document the operator notified the excavator of the inherent hazards in the release of sour gas when responding to requests to mark pipeline location? |  | 33760
192.615(a)_P | Has the operator established written procedures to minimize the hazard resulting from a gas pipeline emergency? |  | 33790
192.615(a)(1)_P | Do procedures provide for receiving, identifying, and classifying notices of events which require immediate response by the operator? |  | 33820
192.615(a)(1)_R | Do records document receiving, identifying, and classifying notices of events which require immediate response by the operator? |  | 33850
192.615(a)(2)_P | Do procedures provide for establishing and maintaining adequate means of communication with appropriate fire, police, and other public officials? |  | 33970
192.615(a)(2)_R | Do records document establishing and maintaining adequate means of communication with appropriate fire, police, and other public officials? |  | 34000
192.615(a)(3)(i)_P | Do procedures require prompt and effective response to gas detected inside or near a building? |  | 34060
192.615(a)(3)(i)_R | Do records document prompt and effective response to gas detected inside or near a building? |  | 34090
192.615(a)(3)(i)_O | Does the operator respond promptly and effectively to gas detected inside or near a building? |  | 34100
192.615(a)(3)(i)_O | Does the operator respond promptly and effectively to gas detected inside or near a building? |  | 34100
192.615(a)(3)(ii)_P | Do procedures require prompt and effective response to fire located near or directly involving a pipeline facility? |  | 34120
192.615(a)(3)(ii)_R | Do records document prompt and effective response to fire located near or directly involving a pipeline facility? |  | 34150
192.615(a)(3)(iii)_P | Do procedures require prompt and effective response to an explosion occurring near or directly involving a pipeline facility? |  | 34180
192.615(a)(3)(iii)_R | Do records document prompt and effective response to an explosion occurring near or directly involving a pipeline facility? |  | 34210
192.615(a)(3)(iv)_P | Do procedures require prompt and effective response to natural disasters? |  | 34240
192.615(a)(3)(iv)_R | Do records document prompt and effective response to natural disasters? |  | 34270
192.615(a)(4)_P | Do procedures require the availability of personnel, equipment, tools, and materials, as needed, at the scene of an emergency? |  | 34300
192.615(a)(5)_P | Do procedures require that emergency actions are directed toward protecting people first and then property? |  | 34360
192.615(a)(6)_P | Do procedures require emergency shutdown and pressure reduction in any section of the pipeline system necessary to minimize hazards to life or property? |  | 34390
192.615(a)(6)_R | Do records document emergency shutdown and pressure reduction in any section of the pipeline system necessary to minimize hazards to life or property? |  | 34420
192.615(a)(7)_P | Do procedures require making safe any actual or potential hazard to life or property? |  | 34450
192.615(a)(8)_P | Do procedures require notifying appropriate fire, police, and other public officials of gas pipeline emergencies and coordinating with them both planned responses and actual responses during an emergency? |  | 34480
192.615(a)(8)_R | Do records document notification of appropriate fire, police, and other public officials of gas pipeline emergencies and coordination with them for both planned responses and actual responses during an emergency? |  | 34510
192.615(a)(9)_P | Do procedures require safely restoring any service outage? |  | 34540
192.615(a)(9)_R | Do records document safely restoring any service outage? |  | 34550
192.615(a)(10)_P | Do procedures require beginning action under 192.617, if applicable, as soon after the end of the emergency as possible? |  | 34553
192.615(a)(10)_P | Do procedures require beginning action under 192.617, if applicable, as soon after the end of the emergency as possible? |  | 34553
192.615(a)(11)_P | Do procedures require actions to be taken by a controller during an emergency in accordance with 192.631? |  | 34560
192.615(a)(11)_P | Do procedures require actions to be taken by a controller during an emergency in accordance with 192.631? |  | 34560
192.615(b)(1)_P | Do procedures require that supervisors responsible for emergency action have been furnished a copy of the latest edition of the emergency procedures? |  | 34570
192.615(b)(1)_R | Do records document that supervisors responsible for emergency action been furnished a copy of the latest edition of the emergency procedures? |  | 34600
192.615(b)(2)_P | Do procedures require that appropriate operating personnel are trained to assure that they are knowledgeable of the emergency procedures and verify that the training is effective? |  | 34630
192.615(b)(2)_R | Do records document that appropriate operating personnel are trained to assure that they are knowledgeable of the emergency procedures and verify that the training is effective? |  | 34660
192.615(b)(2)_O | Are appropriate operating personnel trained to assure that they are knowledgeable of the emergency procedures and verify that the training is effective? |  | 34664
192.615(b)(3)_P | Do procedures require that employee activities are reviewed to determine whether the procedures were effectively followed in each emergency? |  | 34690
192.615(b)(3)_R | Do records document that employee activities are reviewed to determine whether the procedures were effectively followed in each emergency? |  | 34720
192.615(c)_O | Does operator liaison with appropriate fire, police, and other public officials that may respond to a gas pipeline emergency? |  | 34740
192.615(c)(1)_P | Do procedures require liaison with appropriate fire, police, and other public officials to be established and maintained to learn the responsibility and resources of each government organization that may respond to a gas pipeline emergency? |  | 34750
192.615(c)(1)_R | Do records document liaison with appropriate fire, police, and other public officials has been established and maintained to learn the responsibility and resources of each government organization that may respond to a gas pipeline emergency? |  | 34760
192.615(c)(2)_P | Do procedures require liaison with appropriate fire, police, and other public officials to be established and maintained to acquaint the officials with the operator's ability in responding to a gas pipeline emergency? |  | 34780
192.615(c)(2)_R | Do records document liaison with appropriate fire, police, and other public officials has been established and maintained to acquaint the officials with the operator's ability in responding to a gas pipeline emergency? |  | 34790
192.615(c)(3)_P | Do procedures require liaison with appropriate fire, police, and other public officials to be established and maintained to identify the types of gas pipeline emergencies of which the operator notifies the officials? |  | 34810
192.615(c)(3)_R | Do records document liaison with appropriate fire, police, and other public officials has been established and maintained to identify the types of gas pipeline emergencies of which the operator notifies the officials? |  | 34820
192.615(c)(4)_P | Do procedures require liaison with appropriate fire, police, and other public officials to be established and maintained to plan how the operator and officials can engage in mutual assistance to minimize hazards to life or property? |  | 34840
192.615(c)(4)_R | Do records document liaison with appropriate fire, police, and other public officials has been established and maintained to plan how the operator and officials can engage in mutual assistance to minimize hazards to life or property? |  | 34850
R 460.20422_P | SOUR GAS: Do procedures require emergency plans address the hazards inherent with the transportation of sour gas and include plans and procedures to minimize the health risk to the operator's employees and the general public in the event of an emergency of a sour gas system? |  | 34870
R 460.20422_R | SOUR GAS: Do records document the hazards inherent with the transportation of sour gas were addressed to minimize the health risk to the operator's employees and the general public in the event of an emergency of a sour gas system? |  | 34880
R 460.20423(a)_P | SOUR GAS: Do procedures require an operator of pipeline facilities used in the transportation of sour gas continuing education program to enable the public, appropriate government organizations, and persons engaged in excavation-related activities to take appropriate action in the event of an unplanned release of sour gas? |  | 35950
R 460.20423(a)_P | SOUR GAS: Do procedures require an operator of pipeline facilities used in the transportation of sour gas continuing education program to enable the public, appropriate government organizations, and persons engaged in excavation-related activities to take appropriate action in the event of an unplanned release of sour gas? |  | 35950
R 460.20423(b)_P | SOUR GAS: Do procedures require an operator of pipeline facilities used in the transportation of sour gas continuing education program to enable the public, appropriate government organizations, and persons engaged in excavation-related activities to recognize a sour gas pipeline emergency for the purpose of reporting it to the operator or other appropriate public officials? |  | 36010
R 460.20423(b)_P | SOUR GAS: Do procedures require an operator of pipeline facilities used in the transportation of sour gas continuing education program to enable the public, appropriate government organizations, and persons engaged in excavation-related activities to recognize a sour gas pipeline emergency for the purpose of reporting it to the operator or other appropriate public officials? |  | 36010
192.707(a)_P | Do procedures require line markers be placed and maintained as close as practical over each buried main and transmission line at each crossing of a public road and railroad, and wherever necessary to identify the location of the transmission line or main to reduce the possibility of damage or interference? Exceptions: Mains and transmission lines located offshore, or at crossings of or under waterways and other bodies of water. Mains in Class 3 or 4 locations where a damage prevention program is in effect under 192.614. Transmission lines in Class 3 or 4 locations where placement of a line marker is impractical. |  | 38690
192.707(a)_O | Are line markers placed and maintained as close as practical over each buried main and transmission line at each crossing of a public road and railroad, and wherever necessary to identify the location of the transmission line or main to reduce the possibility of damage or interference? Exceptions: Mains and transmission lines located offshore, or at crossings of or under waterways and other bodies of water. Mains in Class 3 or 4 locations where a damage prevention program is in effect under 192.614. Transmission lines in Class 3 or 4 locations where placement of a line marker is impractical. |  | 38700
192.707(c)_P | Do procedures require line markers be placed and maintained along each section of a main and transmission line that is located above ground in an area accessible to the public? |  | 38830
192.707(c)_O | Are line markers placed and maintained along each section of a main and transmission line that is located above ground in an area accessible to the public? |  | 38860
192.707(d)(1)_P | Do procedures require the following be written legibly on a background of sharply contrasting color on each line marker: The word "Warning," "Caution," or "Danger" followed by the words "Gas (or name of gas transported) Pipeline" all of which, except for markers in heavily developed urban areas, must be in letters at least 1" high with ¼" stroke? |  | 38890
192.707(d)(1)_O | Is the following written legibly on a background of sharply contrasting color on each line marker: The word "Warning," "Caution," or "Danger" followed by the words "Gas (or name of gas transported) Pipeline" all of which, except for markers in heavily developed urban areas, must be in letters at least 1" high with ¼" stroke? |  | 38920
192.707(d)(2)_P | Do procedures require the following be written legibly on a background of sharply contrasting color on each line marker: The name of the operator and telephone number (including area code) where the operator can be reached at all times? |  | 38950
192.707(d)(2)_O | Is the following written legibly on a background of sharply contrasting color on each line marker: The name of the operator and telephone number (including area code) where the operator can be reached at all times? |  | 38980
R 460.20427(a)_P | SOUR GAS: Do procedures require line markers be placed and maintained as close as practical over a sour gas pipeline and clearly identify the pipeline as a carrier of sour gas? |  | 39010
R 460.20427(a)_O | SOUR GAS: Are line markers placed and maintained as close as practical over a sour gas pipeline and clearly identify the pipeline as a carrier of sour gas? |  | 39020
R 460.20427(b)_P | SOUR GAS: Do procedures require, where practical, that at least one line marker visible from any location on the sour gas pipeline? |  | 39040
R 460.20427(b)_O | SOUR GAS: Is at least one line marker visible from any location on the sour gas pipeline, where practical? |  | 39050
NTSB Rec. P-000_P | Do distribution operations emergency plans and procedures require employees and contractors who respond to gas leaks to consider the possibility of multiple leaks, to check for gas accumulation in nearby buildings, and, if necessary, to take steps to promptly stop the flow of gas? Are these procedures communicated to both employee and contractor personnel who are responsible for emergency response to pipeline incidents? |  | 62440
NTSB Rec. P-000_R | Do records document that employees and contractors who responded to gas leaks considered the possibility of multiple leaks, checked for gas accumulation in nearby buildings, and, if necessary, took steps to promptly stop the flow of gas? |  | 62450